Mettler-Toledo AG,Process Analytics

M400 2-wire G2 HART Release Notes

Table of Contents

1	HART Device List	3

1.1	AMS, DeltaV list	3

1.2	PDM list	3

2	Revision History	4

3	Installation for different host	5

3.1	AMS, DeltaV	5

3.2	PDM	5

3.3	Other hosts	5

4	Know issues and limitations	6

4.1	General	6

4.2	PDM	6

4.2.1	Manufacturer independent problem	6

# HART Device List

NOTE: This version of DD is NOT certified by FieldComm Group yet.

## AMS, DeltaV list

| Type | Describtion | Dev Rev | DD Rev | Tested AMS version | Tested DeltaV Version | Firmware |
| --- | --- | --- | --- | --- | --- | --- |
| 0x8e71 | M400 2-wire G2 | 02 | 01 | 14.1 | 14.3 | V1.1.00 |

## PDM list

| Type | Describtion | Dev Rev | DD Rev | Tested PDM Version | Firmware |
| --- | --- | --- | --- | --- | --- |
| 0x8e71 | M400 2-wire G2 | 02 | 01 | PDM 8.1, PDM 9.0 | V1.1.00 |

# Revision History

| Version | Description of changes |
| --- | --- |
| V1.00.00 2023/May/17 | Initial Version. |
| V1.01.00 2024/July/8 | 1. Update for M400 2-Wire G2 release version V1.1.00 to support EasyClean related function. The DD version update to 0201(Device_Rev2, DD_Rev1). 2. Add PDM install description. |

# Installation for different host

This chapter describes the standalone installation for different hosts

For AMS software questions, contact the EMERSON Support or refer to the Manual.

For further questions, contact the Mettler-Toledo Support.

## AMS, DeltaV

- Use the DD under folder “1.AMS_DeltaV”. Extract DD files from “.zip” package.

- Close all of AMS application. Use the DD installation utility “Add Device Type”to install the DDs. For the detail steps about DD installation, refer to the AMS related installation manual delivered by Emerson.

- If the version of AMS is not listed in ddinstal.ini file, please modified "AmsVersionSupport=10.5,11.0,11.1,11.5,12.0,14.1,14,5, xx.x",  xx.x is the user’s AMS version. Another solution is to use “Other host, FM8” files.

## PDM

- Use the DD in folder “2.PDM”. Extract DD files from “.zip” package.

- Please close all applications before the installation start.

- Use PDM utility “Device Integration Manager” to install DD, selected install method “Read device descriptions from source directory”.

- Choose the extract DD folder, select items recognized by application, press integration.

## Other hosts

- Use FM8 or FDI package, refer to the host related installation manual.

# Know issues and limitations

## General

- This version of DD is developed to support M400 2-Wire G2 Transmitter EasyClean related function. Currently, it is NOT certified by FieldComm Group. The certified DD version is Device_Rev1, DD_Rev1. The file could be found at FCG(https://www.fieldcommgroup.org/) or MT website(https://www.mt.com/de/en/home/library/software-downloads/process-analytics/m400-2-wire-g2-hart-rev1-dd1.html)

- We recommend performing an “Reload Configuration” after change sensor type or channel. Eg: change pH to O2 sensor.

## PDM

### Manufacturer independent problem

- “Download to Device” is not suggested, this is because some parameters require corresponding sensor connected to transmitter and the write may not take effect. If offline configuration is needed, Mettler Toledo “TCT tool” is a better choice.

- After “Upload to PC/PG”, the display for some of parameters in review menu is incorrect. Some warnings/errors could be generated in the process, just ignore them.