Mettler-Toledo AG,Process Analytics

PA Release Notes

Date 2014-11-04

Table of Contents

1	PA Device List	3

1.1	PDM	3

1.2	DTM list	3

2	Revision History	4

3	Installation for different host	4

3.1	PDM	4

3.2	DTM	4

4	Know issues and limitations	4

4.1	General	4

4.2	PDM	4

4.2.1	Manufacturer independent problem	4

4.3	DTM	4

# PA Device List

## PDM

| Device Type | Dev Rev | DD Rev | Min version | PA-Stack Rev | Transmitter Rev |
| --- | --- | --- | --- | --- | --- |
|  | 1 | 02 | 6.0SP5 | 2.6 | 1.0.00 |

## DTM list

| Type | Describtion | Dev Rev | DD Rev | DTM version | Firmware |
| --- | --- | --- | --- | --- | --- |
|  | M400 PA | 1 | 02 | 1.00.0004 | 1.0.00 |

# Revision History

| Version | Description of changes |
| --- | --- |
| V1.0.01 | 1. Add DTM 2. Optimize for PDM v8.1SP1 |
| V1.00.00 2014/4/15 | First introduced to the package |

# Installation for different host

This chapter describes the standalone installation for different hosts.

## PDM

- Please use the DD under “DD for PDM”

- Please close all applications before the installation

- For SIEMENS PDM Version 6.0 Service Pack 2 or lower use the tool “Manage Device Catalog”.

- For SIEMENS PDM Version 5.2 Service Pack 1 or lower use the “Deviceinstall.exe” in the DD setup package.

## DTM

- None.

# Know issues and limitations

## General

- Please close application(PDM, DTM, ect) and reopen again if changing sensor type over bus Eg: change pH to O2 sensor.

- Re-configure all of AI block when change sensor.

## PDM

### Manufacturer independent problem

- After “Upload to PC/PG”, the display for some of parameters in review menu is incorrect.

- PDM6.0SP5 HF4 – Known Issue updating to HF4

After the update to HF4 it may happen that cannot be opened anymore after installed Profibus devices DD. Please reinstall the original device catalogue to resolve this. Before first time using PDM 6.0 SP5 HF4, please install the PI Library first.

For further questions, please contact the SIEMENS Support.

## DTM

- Close and reopen measurement values screen to refresh the new unit if AI’s parameters are changed