Mettler-Toledo AG,Process Analytics

M400 2-wire CondInd HART

Table of Contents

1	HART Device List	3

1.1	AMS,DeltaV list	3

1.2	PDM list	3

1.3	DTM list	3

2	Revision History	4

3	Installation for different host	5

3.1	AMS,DeltaV	5

3.2	PDM	5

3.3	DTM	5

3.4	HH375,HH475	5

3.5	PRM	5

3.6	Other host	5

4	Know issues and limitations	6

4.1	General	6

4.2	AMS	6

4.2.1	Manufacturer independent problem	6

4.3	PDM	6

4.3.1	Manufacturer independent problem	6

4.4	DTM	6

# HART Device List

## AMS,DeltaV list

| Type | Describtion | Dev Rev | DD Rev | Min AMS version | Min DeltaV version | Firmware |
| --- | --- | --- | --- | --- | --- | --- |
| 0x8e7e | M400 2XH Cond Ind | 1 | 01 | 9.0 | 9.3 | V_1.0.00 |

### Note:only AMS v12.0 is tested and is extend to other versions with list above.

## PDM list

| Type | Describtion | Dev Rev | DD Rev | Min Required version | Firmware |
| --- | --- | --- | --- | --- | --- |
| 0x8e7e | M400 2XH Cond Ind | 1 | 01 | 6.0 SP5 | V_1.0.00 |

### Note:only PDM v8.1 is tested and is extend to other versions with list above.

## DTM list

| Type | Describtion | Dev Rev | DD Rev | DTM version | Firmware |
| --- | --- | --- | --- | --- | --- |
| 0x8e7e | M400 2XH Cond Ind | 1 | 01 | 1.00.2003 | V_1.0.00 |

# Revision History

| Version | Description of changes |
| --- | --- |
| V1.00.01 2020/March/13 Daniel Zhang | - Support new AMS&DeltaV version |
| V1.00.00 | - First introduced to the package. |

# Installation for different host

This chapter describes the standalone installation for different hosts

For PDM software questions, contact the SIEMENS Support or refer to the Manual

For AMS software questions, contact the EMERSON Support or refer to the Manual

For further questions, contact the Mettler-Toledo Support.

## AMS,DeltaV

- Use the DD under “DD for AMS_DeltaV”. Use the DD under “DD for General host” if the AMS version is less than “Min AMS version” that describe above

- Close all of AMS application. Use the DD installation utility “Add Device Type”to install the DDs. For the detail steps about DD installation, refer to the AMS related installation manual delivered by Emerson.

- If the version of AMS is more than v12.0, please modified the ddinstall.ini file "AmsVersionSupport=10.5,11.0,11.1,11.5,12.0,xx.x"

- If the version of DeltaV is less than v9.0, please use the DD under menu "DD for lower version"

## PDM

- Please close all applications before the installation start

- For SIEMENS PDM Version 5.2 Service Pack 1 or lower use the “Deviceinstall.exe” in package.

- For SIEMENS PDM Version 6.0 Service Pack 2 or lower use the tool “Manage Device Catalog”.

## DTM

- Install the DTM drive under “DTM”

## HH375,HH475

- Please use the DD under “DD for HH475,HH375”

- Min System Required version is 3.7

## PRM

- Verify that no PRM or FieldMate is running.

- Use the DD installation utility to install the DDs and device icon(Action Menu\Device Files setup

For this device)

- Copy .cfg and .bmp files into the installation folder(Eg: /PRM/Helper/Device Viewer).

Note: warning could be appear during the installation due to files already are installed.

## Other host

- Use FM6 or FM8 files, refer to the host related installation manual

# Know issues and limitations

## General

- Firmware less than V_1.0.12 have an issue when change channel over HART.

- We recommend performing an upload before the first commissioning. This ensures data consistency with the device and will prevent possible problems during the download.

- We recommend performing an upload  after change sensor type or channel. Eg: change pH to O2 sensor.

## AMS

### Manufacturer independent problem

- Some drivers could not be installed in the AMS version 10.0. This problem is resolved in AMS version 10.1.

For further questions, contact the EMERSON Support or refer to the Manual.

## PDM

### Manufacturer independent problem

- After “Upload to PC/PG”, the display for some of parameters in review menu is incorrect.

- PDM6.0SP5 HF4 – Known Issue updating to HF4

After the update to HF4 it may happen that cannot be opened anymore after installed Profibus devices DD. Please reinstall the original device catalogue to resolve this. Before first time using PDM 6.0 SP5 HF4, please install the PI Library first.

- Toolbar-icon for the process variables is not supported

For further questions, please contact the SIEMENS Support.

## DTM